| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (20HR) | 6V 2Ah |  |
| Dimension | Length Width Container Height Total Height | 42±1mm （1.65 inches) 37±1mm (1.46 inches) 76±1mm (2.99 inches) 76±1mm (2.99 inches) |  |
| Weight | Approx. 0.33Kg ( 0.73lbs) |  |
| Standard Terminal | Copper |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 20 hour rate (100mA) 10 hour rate (180mA) 5 hour rate (340mA) 3 hour rate (500mA) 1hour rate (1200mA) | 2Ah 1.9Ah 1.7Ah 1.5Ah 1.2Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 50mΩ |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 0.69A Voltage 7.20~7.50V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 6.75~6.90V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |