| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (10HR) | 12V 120Ah |  |
| Dimension | Length Width Container Height Total Height | 552±2mm （21.73 inches） 110±2mm (4.33 inches) 239±2mm (9.41 inches) 239±2mm (9.41inches) |  |
| Weight | Approx. 37.5Kg ( 82.65lbs) |  |
| Standard Terminal | Bolt-and-nut terminal Bolt Type: M6 |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 20 hour rate (6A) 10 hour rate (12A) 5 hour rate (20.4A) 3 hour rate (30A) 1hour rate (72A) | 126Ah 120Ah 102Ah 90Ah 72Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 4.3mΩ |  |
| Designed life | ≥10 years (25℃,77 0F) |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 30A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |