| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 2V 10Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 52±1mm (2.05 inches) 52±1mm (2.05 inches) 93±1mm (3.66 inches) 98±1mm (3.86 inches) |  |  |
| Weight |  |  |  | Approx. 0.55 Kg ( 1.21lbs) |  |  |
| Standard Terminal |  |  |  | Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.5A) 10 hour rate (0.9A) 5 hour rate (1.7A) 3 hour rate (2.5A) 1hour rate (6A) |  | 10Ah 9.5Ah 8.5Ah 7.5Ah 6Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 10mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 3.6A Voltage 2.4~2.5V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 2.25~2.3V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |