| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 150Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 485±2mm （19.09 inches） 172±2mm (6.77 inches) 240±2mm (9.45 inches) 240±2mm (9.45 inches) |  |  |
| Weight |  |  |  | Approx. 45Kg (99.18lbs) |  |  |
| Standard Terminal |  |  |  | B3(Bolt-and-nut Lead terminal) Bolt Type: M8 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (15A) 5 hour rate (25.5A) 3 hour rate (37.5A) 1hour rate (90A) |  | 150Ah 128Ah 113Ah 90Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 3mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 37.5A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |