| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 2.2Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 178±1mm （7.01 inches) 35±1mm (1.38 inches) 60±1mm (2.36 inches) 66±1mm (2.60 inches) |  |  |
| Weight |  |  |  | Approx. 0.98Kg ( 2.16lbs) |  |  |
| Standard Terminal |  |  |  | F1-Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.11A) 10 hour rate (0.198A) 5 hour rate (0.374A) 3 hour rate (0.55A) 1hour rate (1.32A) |  | 2.2Ah 2.1Ah 1.9Ah 1.7Ah 1.4Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 50mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 0.66A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |  |  |