| PHYSICAL SPECIFICATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 6V 2.8Ah |  |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 66±1mm （2.60 inches） 34±1mm (1.34 inches) 99±1mm (3.90 inches) 104±1mm (4.09 inches) |  |  |  |
| Weight |  |  |  | Approx. 0.59Kg ( 1.30lbs) |  |  |  |
| Standard Terminal |  |  |  | F1-Fasten Tab No.187E |  |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.14A) 10 hour rate (0.25A) 5 hour rate (0.48A) 1hour rate (1.68A) |  | 2.8Ah 2.7Ah 2.4Ah 1.7Ah |  |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 30mΩ |  |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 0.84A Voltage 7.20~7.50V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 6.75~6.90V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |  |  |  |