| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 20Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 181±1mm （7.13 inches) 77±1mm (3.03 inches) 167±1mm (6.57 inches) 167±1mm (6.57 inches) |  |  |
| Weight |  |  |  | Approx. 6.1 Kg (13.44lbs) |  |  |
| Standard Terminal |  |  |  | Bolt and nut terminal Bolt Type:M5 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (1A) 10 hour rate (1.8A) 5 hour rate (3.4A) 1hour rate (12A) |  | 20Ah 19Ah 17Ah 16Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 92% 84% 75% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 15mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 6A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –30mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –20mV/℃ |  |  |  |