| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 4V 4.5Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 47±1mm (1.85 inches) 47±1mm (1.85 inches) 101±1mm (3.98 inches) 106±1mm (4.17 inches) |  |  |
| Weight |  |  |  | Approx. 0.6Kg (1.32lbs) |  |  |
| Standard Terminal |  |  |  | Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.225A) 10 hour rate (0.405A) 5 hour rate (0.765A) 3 hour rate (1.125A) 1hour rate (2.7A) |  | 4.5Ah 4.2Ah 3.9Ah 3.4Ah 2.7Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 20mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 1.35A Voltage 4.8~5V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 4.5~4.6V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |