| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 65Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 350±1mm （13.78 inches） 167±1mm (6.57 inches) 178±1mm (7.01 inches) 178±1mm (7.01 inches) |  |  |
| Weight |  |  |  | Approx. 21Kg ( 46.28lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut lead terminal Bolt Type: M6 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| Capacity |  |  | 10 hour rate (6.5A) 5 hour rate (11.05A) 3 hour rate (16.25A) 1hour rate (39A) |  | 65Ah 55.5Ah 48.8Ah 39Ah | # Discharge curves @ 25℃ (77 °F) |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 5mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 16.2A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |