| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 8V 7.2Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 164±1mm (6.46 inches) 28±1mm (1.10 inches) 99±1mm (3.90 inches) 104±1mm (4.09 inches) |  |  |
| Weight |  |  |  | Approx. 1.32 Kg ( 2.91lbs) |  |  |
| Standard Terminal |  |  |  | Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.36A) 10 hour rate (0.648A) 5 hour rate (1.224A) 3 hour rate (1.8A) 1hour rate (4.32A) |  | 7.2Ah 6.8Ah 6.2Ah 5.4Ah 4.4Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 20mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 2.1A Voltage 9.6~10V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 9~9.2V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |