| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 2V 150Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 171±2mm （6.73 inches） 102±2mm (4.02 inches) 205±2mm (8.07 inches) 227±2mm (6.94 inches) |  |  |
| Weight |  |  |  | Approx. 9.5 Kg ( 20.9lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nuts terminal Bolt Type: M8 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 100 hour rate (1.5A) 50 hour rate (3A) 10 hour rate (15A) 1hour rate (97.5A) |  | 165Ah 157Ah 150Ah 98Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | ≥4000Cycles @ 20% DOD(25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 0.9mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 37.5A Voltage 2.35~2.40V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 2.25~2.30V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |