| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 2V 2000Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 491±2mm （19.33 inches） 351±2mm (13.82 inches) 344±2mm (13.54inches) 383±2mm (15.08 inches) |  |  |
| Weight |  |  |  | Approx. 159Kg (350.1lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nuts terminal Bolt Type: M8 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 100 hour rate (20A) 50 hour rate (40A) 10 hour rate (200A) 1 hour rate (1300A) |  | 2200Ah 2100Ah 2000Ah 1350Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | ≥4200 Cycles @ 20% DOD (25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 0.15mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 500A Voltage 2.35~2.40V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 2.23V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |