| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 75Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 562±2mm （22.13 inches） 114±2mm (4.49 inches) 188±2mm (7.40 inches) 188±2mm (7.40 inches) |  |  |
| Weight |  |  |  | Approx. 29Kg ( 63.92lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut terminal Bolt Type: M6 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (3.75A) 10 hour rate (7.5A) 5hour rate (12.75A) 3hour rate (18.75A) 1hour rate (45A) |  | 79Ah 75Ah 64Ah 56Ah 45Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 6mΩ |  |  |  |
| Designed life |  |  | ≥10 years (25℃,77 0F) |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 18.75A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |