| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 2V 200Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 173±2mm （6.81 inches） 111±2mm (4.37 inches) 329±2mm (12.95 inches) 365±2mm (14.37 inches) |  |  |
| Weight |  |  |  | Approx. 16.4 Kg (36.15lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nuts terminal Bolt Type: M8 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (10A) 10 hour rate (20A) 5 hour rate (34A) 3 hour rate (50A) 1hour rate (130A) |  | 210Ah 200Ah 170Ah 150Ah 130Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | ≥4200Cycles @ 20% DOD(25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 0.5mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 50A Voltage 2.35~2.40V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 2.23V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |