| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 6V 150Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 260±2mm （10.24 inches） 180±2mm (7.09 inches) 247±2mm (9.72 inches) 254±2mm (10.00 inches) |  |  |
| Weight |  |  |  | Approx. 24.2Kg (53.34lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nuts terminal) Bolt Type: M8 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (7.5A) 10 hour rate (15A) 5 hour rate (25.5A) 3 hour rate (37.5A) 1hour rate (90A) |  | 158Ah 150Ah 127Ah 112.5Ah 90Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | 10 years (floating) or >750 Cycles @ 50% D.O.D |  |  |  |
| Self Discharge |  |  | 3% of capacity declined per month at (25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 3mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 37.5A Voltage 7.05~7.20V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 6.75~6.90V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |  |  |