| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 1.3Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 97±1mm （3.82 inches) 44±1mm (1.73 inches) 53±1mm (2.09 inches) 59±1mm (2.32 inches) |  |  |
| Weight |  |  |  | Approx. 0.58 Kg ( 1.28lbs) |  |  |
| Standard Terminal |  |  |  | F1-Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.065A) 10 hour rate (0.117A) 5 hour rate (0.221A) 3 hour rate (0.325A) 1hour rate (0.78A) |  | 1.3Ah 1.2Ah 1.1Ah 1.0Ah 0.78Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 50mΩ |  |  |  |
| Designed life |  |  | ≥720 Cycles @ 50% DOD (25℃) |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 0.39A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |