| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 10Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 151±1mm （5.94 inches） 99±1mm (3.90 inches) 96±1mm (36.61inches) 101±1mm (3.98 inches) |  |  |
| Weight |  |  |  | Approx. 3.45Kg (7.6lbs) |  |  |
| Standard Terminal |  |  |  | F1-Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.5A) 10 hour rate (0.9A) 5 hour rate (1.7A) 3 hour rate (2.5A) 1hour rate (6A) |  | 10Ah 9.5Ah 8.5Ah 7.5Ah 6Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 23mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 3A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |