### PHYSICAL SPECIFICATION

| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 33Ah |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Dimension |  | Length Width Container Height Total Height |  | 196±1mm （7.72 inches) 130±1mm (5.12 inches) 163±1mm (6.42 inches) 179±1mm (7.05 inches) |  |  |
| Weight |  |  |  | Approx. 11.4 Kg ( 25.1lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut lead terminal Bolt Type: M6 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (3.3A) 5 hour rate (5.61A) 3 hour rate (8.25A) 1hour rate (19.8A) |  | 33Ah 28Ah 25Ah 20Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 10.3mΩ |  |  |  |
| Designed life |  |  | ≥720 Cycles @ 50% DOD (25℃) |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 8.25A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |