| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 38Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 198±2mm （7.80 inches） 166±2mm (6.53 inches) 170±2mm (6.69 inches) 170±2mm (6.69 inches) |  |  |
| Weight |  |  |  | Approx. 13.1Kg ( 28.85lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut lead terminal Bolt Type: M6 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (3.8A) 5 hour rate (6.46A) 3 hour rate (9.5A) 1hour rate (22.8A) |  | 38Ah 32.3Ah 28.5Ah 22.8Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | ≥720 Cycles @ 50% DOD (25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F)10.1mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 9.5A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |