| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 70Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 259±2mm （10.20 inches） 168±2mm (6.61 inches) 208±2mm (8.19 inches) 212±2mm (8.35 inches) |  |  |
| Weight |  |  |  | Approx.23.9Kg (52.63lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut terminal Bolt Type: M6 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (7.0A) 5hour rate (11.9A) 3hour rate (17.5A) 1hour rate (42A) |  | 70Ah 60Ah 52.5Ah 42Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Designed life |  |  | ≥720 Cycles 50% DOD (25℃) |  |  |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F)5.7mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 17.5A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |

| Cycle Service Life |  |  |  |  | Trickle (or Float) Service Life |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Storage Time (months) |  |  |  |  | Effect of temperature on capacity |  |  |  |  |  |  |  |  |  |
| Charging Time (Hours) |  |  |  |  | Charging Procedures(12V series) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Application | Charging Voltage(V/Cell) |  |  |  |  |  |  | Max Charge Current |  |
|  |  |  |  |  |  | Temperature |  | Set point |  |  | Allowable range |  |  |  |
|  |  |  |  |  | Cycle Use | 0.25℃ (77℉) |  | 14.2 |  |  | 14.1~~14.3 |  | 0.25C |  |
|  |  |  |  |  | Standby | 0.25℃ (77℉) |  | 2.275 |  |  | 2.25~~2.3 |  | 0.25C |  |
| Charging procedures (6V series) |  |  |  |  | Discharge Current VS. Discharge Voltage |  |  |  |  |  |  |  |  |  |
| Application | Charging Voltage(V) |  |  | Max Charge Current | Final Discharge Voltage (V/Cell) |  | 1.75 |  | 1.7 |  |  | 1.55 |  | 1.3 |
|  | Temperature | Set point | Allowable range |  |  |  |  |  |  |  |  |  |  |  |
| Cycle Use | 0.25℃(77℉) | 7.1 | 7.05~~7.15 | 0.25C |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Discharge Voltage (V/Cell) |  | 0.2C＞（A） |  | 0。2C＜（A）＜ 0。5C |  |  | 0。5C＜（A）＜1。0C |  | （A）＞ 1。0C |
| Standby | 0.25℃(77℉) | 6.85 | 6.8~~6.9 | 0.25C |  |  |  |  |  |  |  |  |  |  |
| Charge the batteries at least once every twelve months ,if they are stored at 25℃ |  |  |  |  | Charging Method： |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Constant Voltage |  |  |  |  | 14.1~~14.3V,5~~11h,Max.Current 0.1CA |  |  |  |  |
|  |  |  |  |  | Constant Current |  |  |  |  | 0.05CA*2h |  |  |  |  |
| Zhongshan Shimastu Electronic Technology Co., Ltd ADD: Nan Sui Industrial Zone , Nantou Town , Zhongshan ,Guang Dong , China Website: www.shimastu.com Tel:+86-760-3133619 Fax:+86-760-3133629 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |