| PHYSICAL SPECIFICATION |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 4Ah |  |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 114±1mm （4.41 inches） 69±1mm (2.72 inches) 89±1mm (3.5 inches) 89±1mm (3.5 inches) |  |  |  |
| Weight |  |  |  | Approx. 1.58Kg (3.48lbs) |  |  |  |
| Standard Terminal |  |  |  | F1-Fasten Tab M01 |  |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (0.4A) 5 hour rate (0.68A) 3 hour rate (1.0A) 1hour rate (2.4A) |  |  | 4Ah 3.4Ah 3Ah 2.4Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 15mΩ |  |  |  |  |
| Discharge at 32A for 5 seconds (-10℃) |  |  |  |  | ≥9.3V |  |  |
| Discharge at 32A for 90seconds (-10℃) |  |  |  |  | ≥6V |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 1.2A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |  |