| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 2.3Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 113±1mm （4.45 inches） 38±1mm (1.50 inches) 85±1mm (3.35 inches) 85±1mm (3.35 inches) |  |  |
| Weight |  |  |  | Approx. 0.89 Kg ( 1.96lbs) |  |  |
| Standard Terminal |  |  |  | Fasten Tab |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (0.23A) 5 hour rate (0.391A) 3 hour rate (0.575A) 1hour rate (1.38A) |  | 2.3Ah 2.0Ah 1.75Ah 1.4Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Discharge at 18.4A for 5 seconds (-10℃) |  |  |  |  | ≥9.3V |  |
| Discharge at 18.4A for 90seconds (-10℃) |  |  |  |  | ≥6V |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 40mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 0.69A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |  |  |