Shimastu

NPL SERIES

NPL40-12,12V40Ah        FEATURES

VALVE REGULATED LEAD ACID BATTERY FOR LONG LIFE (10YEARS) APPLICATIONS 12V40AH@10HR RATE

· One-way pressure -relief vent for safety and long life.

· Glue seal case-to-cover bond to eliminate leakage.

· Absorbent Glass Mat (AGM) technology for efficient gas recombination of up to 99% and freedom from electrolyte maintenance

· UL -recognized component

· Monticello design for economy of installation and maintenance.

· Can be mounted in any orientation.

· Computer designed lead, low calcium alloy grid for minimal gassing and ease of recycling.

· Case and cover available in ABS

Constant Power Discharge Ratings－ Watts Per Cell @ 77°F(25℃)

| End Point Volts/Cell | Operating Time to End Point Voltage |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5min | 15min | 30min | 1h | 2h | 3h | 5h | 8h | 10h | 20h |
| 9.6V | 1411 | 705 | 443 | 278 | 187 | 116 | 86.1 | 59.6 | 50 | 25.9 |
| 10.2V | 1281 | 693 | 432 | 271 | 174 | 113 | 84 | 56.7 | 47.8 | 24.3 |
| 10.8V | 1089 | 644 | 431 | 250 | 170 | 109 | 81.5 | 54.6 | 45.3 | 22.6 |

Zhongshan Shimastu Electronic Technology Co,Ltd.

Nansui Industrial.Zone,Nantou Town,Zhongshan,Guangdong,P.R.China

Website：Http//www.shimastu.com

E-mail：info@shimastu.com

Tel：+86-760-3133584    Fax：+86-760-3133629

NPL40-12,12V40Ah

Dimensions in mm:

198*166*172*172

*All dimensions in millimeters.

All dimensions are for reference only.

##### NPL40-12,12V40Ah-Specifications

| Cells Per Unit | Voltage Per Unit | Weight | Electrolyte | Maximum Discharge Current | Internal Resistance |
| --- | --- | --- | --- | --- | --- |
| 6 | 12.90V | 30.83Ibs. 14kg | Absorbed H2SO4 SG=1.30g/ml,20℃ | 220 Amps | 7mΩ@25℃ Full Charge |

| ###### Capacity | 40 Ah @ 10 hr. rate to 1.80 volts per cell @ 77°F (25℃). |
| --- | --- |
| Operating Temperature Range | Discharge:-40°F(-40℃)to ＋157°F(69℃). Charge:-10°F(-23℃)to ＋140°F(60℃) (with temperature compensation) |
| Nominal Operating Temperature Range | ＋74°F(23℃) to ＋80°F(27℃) |
| Float Charging Voltage | 13.5 to 13.8 VDC/unit Average at 77°F(25℃). |
| Recommended Maximum Charging Current Limit | C/5 amperes (8 amperes @ 100% depth of discharge) @ 10 hour rate. |
| Equalization and Cycle Service Charging Voltage | 14.4 to 14.8 VDC/unit Average at 77°F(25℃). |
| Maximum AC Ripple (Charge) | 0.5% RMS or 1.5% P-P of float charge voltage recommended for best results Maximum voltage allowed = 1.4% RMS (4% P-P) Maximum current allowed = 2 Amperes RMS (C/20). |
| Self Discharge | Shimastu NPL batteries may be stored for up to 6 months at 77°F(25℃) and then a freshening charges required. For higher temperatures the time interval will be shorter. |
| Accessories | Inter unit connectors; racks and cabinet systems are available. |

Constant Current Discharge Ratings－ Amperes @ 77°F(25℃)

| End Point Volts/Cell | Operating Time to End Point Voltage |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5min | 15min | 30min | 1h | 2h | 3h | 5h | 8h | 10h | 20h |
| 9.6V | 147 | 73.5 | 46.2 | 27.3 | 19.2 | 11.7 | 8.4 | 5.4 | 4.5 | 2.3 |
| 10.2V | 125 | 68 | 42.4 | 26 | 18.7 | 10.8 | 8.1 | 5.2 | 4.4 | 2.2 |
| 10.8V | 101 | 59.6 | 39.9 | 23.1 | 16.8 | 9.9 | 7.5 | 4.9 | 4.2 | 2.1 |

Note: Batteries to be mounted with 0.5 in (1.25 cm) spacing minimum and free air ventilation. Specifications subject to change without notification.