Shimastu

NPL SERIES

NPL200-12,12V200Ah        FEATURES

VALVE REGULATED LEAD ACID BATTERY FOR LONG LIFE (10YEARS) APPLICATIONS 12V200AH@10HR RATE

· One-way pressure -relief vent for safety and long life.

· Glue seal case-to-cover bond to eliminate leakage.

· Absorbent Glass Mat (AGM) technology for efficient gas recombination of up to 99% and freedom from electrolyte maintenance

· UL -recognized component

· Monticello design for economy of installation and maintenance.

· Can be mounted in any orientation.

· Computer designed lead, low calcium alloy grid for minimal gassing and ease of recycling.

· Case and cover available in ABS

Constant Power Discharge Ratings－ Watts Per Cell @ 77°F(25℃)

| End Point Volts/Cell | Operating Time to End Point Voltage |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5min | 15min | 30min | 1h | 2h | 3h | 5h | 8h | 10h | 20h |
| 9.6V | 7392 | 3696 | 2323 | 1458 | 981 | 609 | 451 | 312 | 261 | 135 |
| 10.2V | 6710 | 3634 | 2266 | 1419 | 913 | 592 | 440 | 297 | 251 | 128 |
| 10.8V | 5702 | 3373 | 2257 | 1307 | 891 | 570 | 427 | 286 | 237 | 119 |

Zhongshan Shimastu Electronic Technology Co,Ltd.

Nansui Industrial.Zone,Nantou Town,Zhongshan,Guangdong,P.R.China

Website：Http//www.shimastu.com

E-mail：info@shimastu.com

Tel：+86-760-3133584    Fax：+86-760-3133629

NPL200-12,12V200Ah

Dimensions in mm:

522*238*218*245

*All dimensions in millimeters.

All dimensions are for reference only.

##### NPL200-12,12V200Ah-Specifications

| Cells Per Unit | Voltage Per Unit | Weight | Electrolyte | Maximum Discharge Current | Internal Resistance |
| --- | --- | --- | --- | --- | --- |
| 6V | 12.90V | 139.95Ibs. 63.5kg | Absorbed H2SO4 SG=1.30g/ml,20℃ | 1100 Amps | 3mΩ@25℃ Full Charge |

| ###### Capacity | 200 Ah @ 10 hr. rate to 1.80 volts per cell @ 77°F (25℃). |
| --- | --- |
| Operating Temperature Range | Discharge:-40°F(-40℃)to ＋157°F(69℃). Charge:-10°F(-23℃)to ＋140°F(60℃) (with temperature compensation) |
| Nominal Operating Temperature Range | ＋74°F(23℃) to ＋80°F(27℃) |
| Float Charging Voltage | 13.5 to 13.8 VDC/unit Average at 77°F(25℃). |
| Recommended Maximum Charging Current Limit | C/5 amperes (40 amperes @ 100% depth of discharge) @ 10 hour rate. |
| Equalization and Cycle Service Charging Voltage | 14.4 to 14.8 VDC/unit Average at 77°F(25℃). |
| Maximum AC Ripple (Charge) | 0.5% RMS or 1.5% P-P of float charge voltage recommended for best results Maximum voltage allowed = 1.4% RMS (4% P-P) Maximum current allowed = 20 Amperes RMS (C/10). |
| Self Discharge | Shimastu NPL batteries may be stored for up to 6 months at 77°F(25℃) and then a freshening charges required. For higher temperatures the time interval will be shorter. |
| Accessories | Inter unit connectors; racks and cabinet systems are available. |

Constant Current Discharge Ratings－ Amperes @ 77°F(25℃)

| End Point Volts/Cell | Operating Time to End Point Voltage |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5min | 15min | 30min | 1h | 2h | 3h | 5h | 8h | 10h | 20h |
| 9.6V | 700 | 350 | 220 | 130 | 92 | 56 | 40 | 26 | 22 | 11.4 |
| 10.2V | 596 | 324 | 202 | 124 | 89 | 52 | 38 | 25.6 | 21.4 | 11 |
| 10.8V | 480 | 284 | 190 | 110 | 80 | 48 | 36 | 24 | 20 | 10 |

Note: Batteries to be mounted with 0.5 in (1.25 cm) spacing minimum and free air ventilation. Specifications subject to change without notification.